# CHILLERS PREVENTIVE MAINTENANCE SCHEDULE

| PROCEDURE | WEEKLY | MONTHLY | YEARLY |
| --- | --- | --- | --- |
| 1. Check system operating pressures and temperatures. | x |  |  |
| 2. Check oil level. | x |  |  |
| 3. Check condition of oil. |  | x |  |
| 4. Check liquid injection operation. |  | x |  |
| 5. Check operation of capacity control device (slider & solenoid valves) |  | x |  |
| 6. Check crankcase heater operation. |  | x |  |
| 7. Sample compressor oil. |  |  | x |
| 8. Check integral check valve |  |  | x |
| 9. Check pressure relief valve and roller bearings |  |  | x |
| 10. Check for pipework damages Near to Chiller. |  | x |  |
| 11. Check filter drier |  | x |  |
| 12. Check for leaks (complete leak check) |  |  | x |
| 13. Check liquid line sight glass / moisture indicator | x |  |  |
| 14. Check suction superheat at compressor | x |  |  |
| 15. Check condenser liquid subcooling | x |  |  |
| 16. Check expansion valves, solenoid valves and check valves. |  | x |  |
| 17. Check condenser coils for dirt / debris and clean as required. |  | x |  |
| 18 Check fans and fan guards. |  | x |  |
| 19. Check fan motor bearings. |  |  | x |
| 20. Check water flow. |  | x |  |
| 21. Check water pressure drop & cooler efficiency. |  | x |  |
| 22. Check cooler heater operation (if provided). |  | x |  |
| 23. Check water pH / glycol strength. |  |  | x |
| 24. Check condition of control panel and all components |  | x |  |
| 25. Check power and control wiring. |  | x |  |
| 26. Check sensor locations. |  | x |  |
| 27. Check mechanical HP cut-outs and water flow switch operation. |  | x |  |
| 28. Check under voltage monitor and main disconnect. |  | x |  |
| 29. Check tightness of all wiring connections |  |  | x |
| 30. Check compressor contactors/ overloads/ breakers. |  |  | x |
| 31. Check fan contactors / breakers. |  |  | x |
| 32. Check sensor / transducer calibration |  |  | x |
| 33. Check compressor motor protectors. |  |  | x |
| 34. Check contactor contacts. |  |  | x |
| 35. Check fault history | x |  |  |
| 36. Check operating set points. |  | x |  |
| 37. Check HP and OP safety cut-out function. |  | x |  |
| 38. Check pump-down function. |  |  | x |
| 39. Check capacity load / unload function. |  |  | x |
| 40. Check fan control function. |  |  | x |
| 41. Check ambient cut-out function. |  |  | x |
| 42. Check thermal insulation on cooler and piping. |  | x |  |
| 43. Check vibration isolators, repair/replace as necessary |  | x |  |
| 44. Check unit structure for loose bolts/ screws and tight as necessary |  |  | x |
| 45. Check for rusted/dented/ damaged body parts and repair/ repaint as necessary. |  |  | x |