## COVER
WWW.MEPEXTRA.COM
CONTENTS >>
WATER SUPPLY SYSTEMS
&
DRAINAGE SYSTEMS
WATER SUPPLY SYSTEMS >>
1- Cold / Hot water supply pipe sizing
2- Domestic water Booster pump design
3- Domesting water Transfer pump design
4- Domesting hot water Circulation pump design
5- Eletrical Water Heater sizing
6- Domestic water Tank sizing
DRAINAGE SYSTEMS >>
1- Drainage and Vent pipe sizing
2- Rain water pipe sizing
3- Submersible pump and Sump pit design
4- Septic Tank sizing
5- Grease Interceptor sizing
6- Sump pump discharge pipe - Reversed Pressure Drop (RPD) calculation
CONSULTING >>
MEP_Design Work
Plumbing Calculations Sheets

## HWCP CALCULATION OPT#1
HOT WATER CIRCULATION PUMP (PUMP NO.)
Project Name | Bldg. Name and Bldg. Number |  |  |  |  | Date
Calculation | Hot Water Circulation Pump |  |  |  |  | Engineer
References code: ASPE
| Temperature Drop (ΔT˚ F) | BTU/GPM Relationship
whereas (ΔT˚ F): = | 5 | 2500 btu/hr = 1 GPM
| 10 | 5000 btu/hr = 1 GPM
| 15 | 7500 btu/hr = 1 GPM
| 20 | 10000 btu/hr = 1 GPM
Consider 20˚ Temperature drop as per ASHRAE handbook
Flow Rate Calculations:
As per ASHRAE APP 2019 (IP):---
The approximate total length of all hot water supply and return piping |  |  |  |  | = | 2974 | ft
Equivalent length of pipe fittings |  |  |  |  | = | 20% | from the total pipe length
Total Length of return pipes & Fittings (Approximate) |  |  |  |  | = | 3569
Approximate total heat loss (insulated pipe) |  | = | 3569 ft x 30 (btu/hr)/ft |  | = | 107070 | btu/hr
Total Heat Loss |  | = | 107070 (btu/hr) / 10,000 |  | = | 10.707 | gpm
Pump flow rate |  | = | 11 | gpm
Required Pump Flow Rate |  | = | 14 | gpm |  | Adding Safety Factor (20%)
|  | = | 3.2 | m3/hr
|  | = | 1 | l/s
Pressure Calculations:
Length of farthest return pipe (Approximate) |  |  |  |  | 974 | m
Equivalent length of pipe fittings |  |  |  |  | 20% | From the total pipe length
Total Length of return pipes & Fittings (Approximate) |  |  |  |  | 1169 | m
Average head loss per meter |  |  |  |  | 250 | Pa/m | As per 2009 ASHRAE Handbook Fundamentals (SI)
OR Pump selection catalogues
Friction loss |  |  |  |  | 29.225 | m
Required pump head |  |  |  | = | 30 | m
Length of farthest return pipe (Approximate) |  |  |  |  | 4000 | ft
Equivalent length of pipe fittings |  |  |  |  | 20% | From the total pipe length
Total Length of return pipes & Fittings (Approximate) |  |  |  |  | 4800 | ft
Average head loss per meter |  |  |  |  | 2.5 | ft/100ft | As per 2001 ASHRAE Fundamentals Handbook (IP)
OR Pump selection catalogues
Friction loss |  |  |  |  | 120 | ft
Required pump head |  |  |  | = | 37 | m
Power Calculations:
Density |  |  |  |  | 1000
Gravitational Force |  |  |  |  | 9.81
Pump Efficiency |  |  |  |  | 60% | From Catalogs
Required Pump Power (Each) (kW) |  |  |  |  | 0.4905 | KW
Selection: | PLEASE SELECT (H, Q) REQUIRED FOR YOUR PUMP
Note on A20: Abdelraouf Muhammad: POINT_(2) A rough estimation can be made by multiplying the total length of covered pipe by 30 Btu/h·ft or uninsulated pipe by 60 Btu/h·ft. Table 2 gives actual heat losses in pipes at a service water temperature of 140°F and ambient temperature of 70°F. The values of 30 or 60 Btu/h·ft are only recommended for ease in calculation.
Note on E20: Abdelraouf Muhammad: ASHRAE APPLICATIONS 2019 IP - CH. (51): SERVICE WATER HEATING_PAGE (51.6)
Note on G30: Abdelraouf Muhammad: Range between (10% - 30%) for equivelant length and as per ASHRAE Fundamentals will be between (15% -20%)
Note on G32: Abdelraouf Muhammad: General Design Range: The general range of pipe friction loss used for design of hydronic systems is between 100 and 400 Pa/m of pipe. A value of 250 Pa/m represents the mean to which most systems are designed. Wider ranges may be used in specific designs if certain precautions are taken.
Note on H32: Abdelraouf Muhammad: Convert from Pa/m To Meter to get losses in (m)
Note on I32: Abdelraouf Muhammad: Chapter (22), Page (6), Section: (Range of Usage of Pressure Drop Charts)
Note on G38: Abdelraouf Muhammad: Range between (10% - 30%) for equivelant length and as per ASHRAE Fundamentals will be between (15% -20%)
Note on G40: Abdelraouf Muhammad: General Design Range: The general range of pipe friction loss used for design of hydronic systems is between 1 and 4 ft of water per 100 ft of pipe. A value of 2.5 ft/100 ft represents the mean to which most systems are designed. Wider ranges may be used in specific designs if certain precautions are taken.
Note on H40: Abdelraouf Muhammad: Divide 2.5 / 100 to get losses in (ft)
Note on I40: Abdelraouf Muhammad: Chapter (35), Page (5), Section: (Range of Usage of Pressure Drop Charts)

## HWCP CALCULATION OPT#2
HOT WATER CIRCULATION PUMP (PUMP NO.)
Project Name | Bldg. Name and Bldg. Number |  |  |  |  | Date
Calculation | Hot Water Circulation Pump |  |  |  |  | Engineer
References code: ASPE
| Temperature Drop (ΔT˚ F) | BTU/GPM Relationship
whereas (ΔT˚): = | 5 | 2500 btu/hr = 1 GPM
| 10 | 5000 btu/hr = 1 GPM
| 15 | 7500 btu/hr = 1 GPM
| 20 | 10000 btu/hr = 1 GPM
Consider 20˚ Temperature drop as per ASPE handbook
Flow Rate Calculations:
AS PER\ ASHRAE APP 2019 (IP), ASPE VOL. (2) CHAPTER (6) & ALFRED STEELE CH(17):---
Insert Pipe Length & Size For Supply Network as We Don`t Know the Return Pipe Size:
| Pipe Size (inch) |  | Length in (meter) | Total Length | Q loss (btu/hr) |  | Q loss HWR (btu/hr)
| Pipe Diameter |  |  |  | Length in meter
| Length of 1/2 " pipe |  | 500 | 550 | 8250 |  | Assume the heat loss from return pipes equal to (2/3) heat loss from supply pipes as per ASPE & ASHRAE codes
| Length of 3/4 " pipe | = | 220 | 242 | 4114
| Length of 1 " pipe | = | 350 | 385 | 7315
| Length of 1-1/4 " pipe | = | 320 | 352 | 7392
| Length of 1-1/2 " pipe | = | 260 | 286 | 7150
| Length of 2 " pipe | = | 160 | 176 | 4928
| Length of 2-1/2 " pipe | = | 400 | 440 | 14080
| Length of 3 " pipe | = | 250 | 275 | 10450
| Length of 4 " pipe | = | 0 | 0 | 0
| Length of 5" pipe | = | 0 | 0 | 0
| Length of 6 " pipe | = | 0 | 0 | 0
| Length of 8 " pipe | = | 0 | 0 | 0
| Total Heat loss From Supply Pipes |  |  |  | 63679 |  | 42453
Consider 20˚ Temperature drop as per ASHRAE handbook
Approximate total heat loss (insulated pipe) |  | = | 106132
Total Heat Loss |  | = | 106132 (btu/hr) / 10,000 |  | = | 10.6132 | gpm
Pump flow rate |  | = | 11 | gpm
Required Pump Flow Rate |  | = | 14 | gpm |  | Adding Safety Factor (20%)
|  | = | 3.2 | m3/hr
|  | = | 1 | l/s
Pressure Calculations: | [7 empty] | Feet
Length of farthest return pipe (Approximate) |  |  |  |  | 974 | m
Equivalent length of pipe fittings |  |  |  |  | 20% | From the total pipe length
Total Length of return pipes & Fittings (Approximate) |  |  |  |  | 1169 | m
Average head loss per meter |  |  |  |  | 250 | Pa/m | As per 2009 ASHRAE Handbook Fundamentals (SI)
OR Pump selection catalogues
Friction loss |  |  |  |  | 29.225 | m
Required pump head |  |  |  | = | 30 | m
Length of farthest return pipe (Approximate) |  |  |  |  | 4000 | ft
Equivalent length of pipe fittings |  |  |  |  | 20% | From the total pipe length
Total Length of return pipes & Fittings (Approximate) |  |  |  |  | 4800 | ft
Average head loss per meter |  |  |  |  | 2.5 | ft/100ft | As per 2001 ASHRAE Fundamentals Handbook (IP)
OR Pump selection catalogues
Friction loss |  |  |  |  | 120 | ft
Required pump head |  |  |  | = | 37 | m
Power Calculations:
Density |  |  |  |  | 1000
Gravitational Force |  |  |  |  | 9.81
Pump Efficiency |  |  |  |  | 60% | from catalogs
Required Pump Power (Each) (kW) |  |  |  |  | 0.60495 | KW
Selection: | Duplex Pump Set; each 14 gpm flow @ 37 m head with 1 KW each; (1-Working + 1 Standby)
Note on A36: Abdelraouf Muhammad: Flow Calculation Steps as per all codes mentioned above and if you are using ASHRAE you can find All steps @ 2019 ASHRAE Handbook—HVAC Applications - CH_(51) - Pages_(51.6-51.7) Hot-Water Recirculation Loops and Return Piping:-
Note on G46: Abdelraouf Muhammad: Range between (10% - 30%) for equivelant length and as per ASHRAE Fundamentals will be between (15% -20%)
Note on G48: Abdelraouf Muhammad: General Design Range: The general range of pipe friction loss used for design of hydronic systems is between 100 and 400 Pa/m of pipe. A value of 250 Pa/m represents the mean to which most systems are designed. Wider ranges may be used in specific designs if certain precautions are taken.
Note on H48: Abdelraouf Muhammad: Convert from Pa/m To Meter to get losses in (m)
Note on I48: Abdelraouf Muhammad: Chapter (22), Page (6), Section: (Range of Usage of Pressure Drop Charts)
Note on G54: Abdelraouf Muhammad: Range between (10% - 30%) for equivelant length and as per ASHRAE Fundamentals will be between (15% -20%)
Note on G56: Abdelraouf Muhammad: General Design Range: The general range of pipe friction loss used for design of hydronic systems is between 1 and 4 ft of water per 100 ft of pipe. A value of 2.5 ft/100 ft represents the mean to which most systems are designed. Wider ranges may be used in specific designs if certain precautions are taken.
Note on H56: Abdelraouf Muhammad: Divide 2.5 / 100 to get losses in (ft)
Note on I56: Abdelraouf Muhammad: Chapter (35), Page (5), Section: (Range of Usage of Pressure Drop Charts)

## HWR PIPE SIZE
HWR PIPE SIZER
Project Name | Bldg. Name and Bldg. Number | [6 empty] | Date | 2022-11-02
Calculation | Hot Water Retuen Pipe Sizing Calculation. | [6 empty] | Engineer
DATA ENTRY |  |  | HWR_PIPE SIZING
SEGMENTS | HWR QTY PERCENTAGE | Q (gpm) | Q (l/s) | V (m/S) | Ø int. (mm) | Ø ext. (mm) | Ø nominal. (mm) | Ø nominal. (in) | V (ft/S)
| % | gallon/minute | liter/second | meter/second | millimeter | millimeter | millimeter | inch | feet/second
| 10% | 0.94 | 0.059 | 0.36 | 14.4 | 20 | Ø 20 mm | 0.75 | 1.181
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0.94 | 0.059 | 0.23 | 18 | 25 | Ø 25 mm | 1 | 0.755
| 10% | 0 | 0 | 0 | 18 | 25 | Ø 25 mm | 1 | 0
| 10% | 0 | 0 | 0 | 18 | 25 | Ø 25 mm | 1 | 0
| 10% | 0 | 0 | 0 | 18 | 25 | Ø 25 mm | 1 | 0
| 10% | 0 | 0 | 0 | 18 | 25 | Ø 25 mm | 1 | 0
| 10% | 0 | 0 | 0 | 18 | 25 | Ø 25 mm | 1 | 0
| 10% | 0 | 0 | 0 | 18 | 25 | Ø 25 mm | 1 | 0
| 10% | 0 | 0 | 0 | 18 | 25 | Ø 25 mm | 1 | 0
| 10% | 0 | 0 | 0 | 18 | 25 | Ø 25 mm | 1 | 0
| 10% | 0 | 0 | 0 | 14.4 | 20 | Ø 20 mm | 0.75 | 0

## ASPE DATA SHEET
|  | HOT WATER SUPPLY PIPING | [5 empty] | HOT WATER RETURN PIPING
| Dr Steel-Engineered Plumbing Design II - Table 17-1 Piping HeatLoss (Btu/hr. Per Lineal Ft. For 140°F. Water Temp and 70°F. Room Temp.) | [5 empty] | Dr Steel-Engineered Plumbing Design II - Table 17-1 Piping HeatLoss (Btu/hr. Per Lineal Ft. For 140°F. Water Temp and 70°F. Room Temp.) | [5 empty] | btu/hr | temp C˚
[13 empty] | 2500 | 5˚ | btu/hr |  | FROM | TO | AT
[13 empty] | 5000 | 10˚ | gpm |  | GPM | BTU/HR | TEMP DROP C˚
| NOMINAL PIPE SIZE (INCHES) | INSULATED PIPE 0.5 in | BARE PIPE |  |  |  | NOMINAL PIPE SIZE (INCHES) | INSULATED PIPE 0.5 in | BARE PIPE |  |  |  | 7500 | 15˚ |  |  | 1 | 10000 | 20˚
|  |  | SCHED. 40 STEEL | BRASS, COPPER, T.P. | TYPE (K) COPPER |  |  |  | SCHED. 40 STEEL | BRASS, COPPER, T.P. | TYPE (K) COPPER |  | 10000 | 20˚
Conversion Data
[17 empty] | btu/hr | gpm
| 0.5 | 15 | 35 | 26 | 19 |  | 0.5 | 10 | 24 | 18 | 13 |  |  |  |  | INPUT | 106132 | 11
| 0.75 | 17 | 43 | 32 | 26 |  | 0.75 | 12 | 29 | 22 | 18 |  |  |  |  | INPUT | 107070 | 11
| 1 | 19 | 53 | 38 | 32 |  | 1 | 13 | 36 | 26 | 22
| 1.25 | 21 | 65 | 46 | 39 |  | 1.25 | 14 | 44 | 31 | 26
| 1.5 | 25 | 73 | 53 | 46 |  | 1.5 | 17 | 49 | 36 | 31 |  |  |  | Temperature Drop |  | BTU/GPM Relationship
| 2 | 28 | 91 | 65 | 58 |  | 2 | 19 | 61 | 44 | 39 |  |  |  | 5˚ |  | 2500 B/Hr = 1 GPM
| 2.5 | 32 | 108 | 75 | 68 |  | 2.5 | 22 | 72 | 50 | 46 |  |  |  | 10˚ |  | 5000 B/Hr = 1 GPM
| 3 | 38 | 129 | 90 | 81 |  | 3 | 26 | 86 | 60 | 54 |  |  |  | 15˚ |  | 7500 B/Hr = 1 GPM
| 4 | 46 | 163 | 113 | 103 |  | 4 | 31 | 109 | 76 | 69 |  |  |  | 20˚ |  | 10000 B/Hr = 1 GPM
| 5 | 55 | 199 | 138 | 127 |  | 5 | 37 | 133 | 92 | 85
| 6 | 63 | 233 | 161 | 149 |  | 6 | 42 | 156 | 108 | 100
| 8 | 80 | 299 | 201 | 188 |  | 8 | 54 | 200 | 134 | 126
WHEREAS:
HEAT LOSSES OF HWR PIPING = (2/3) FROM HEAT LOSSES OF HWS PIPING
as per ASPE code
As per ASHRAE APP handbook 2019 IP (chapter 51) page (51.7)
| The Heat loss through pipes according to ASHRAE applications = 30 (btu/hr)/ft | [5 empty] | for insulated pipes |  |  | The required flow rate formula is: GPM = BTU/h/(ΔT X 500)
| The Heat loss through pipes according to ASHRAE applications = 60 (btu/hr)/ft | [5 empty] | for uninsulated pipes
| Fig.1 | [11 empty] | appartement house | club | hospital | hotels | GYM | industerial | office building | private residence | school | YMCA
[12 empty] | private lav. | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2 | 2
[12 empty] | public lav. | 4 | 6 | 6 | 8 | 8 | 12 | 6 |  | 15 | 8
[12 empty] | bathtub | 20 | 20 | 20 | 20 | 30 |  |  | 20 |  | 30
[12 empty] | dishwasher | 15 | 100 | 100 | 125 |  | 60 |  | 15 | 60 | 60
[12 empty] | foot basin | 3 | 3 | 3 | 3 | 12 | 12 |  | 3 | 3 | 12
|  |  | OPT#1 | [8 empty] | kitchen sink | 10 | 20 | 20 | 30 |  | 20 | 20 | 10 | 20 | 20
Calculated Pump Power (Each) (kW) | [5 empty] | 0.436 |  | Meter | 10% |  |  | laundry | 20 | 28 | 28 | 28 |  |  |  | 20 |  | 28
[6 empty] | 0.5 |  | Feet | 15% |  |  | pantry sink | 5 | 10 | 10 | 10 |  | 225 | 10 | 5 | 10 | 10
[9 empty] | 20% |  |  | shower | 30 | 150 | 75 | 75 | 225 | 20 | 30 | 30 | 225 | 225
|  |  | OPT#2 | [5 empty] | 25% |  |  | service sink | 20 | 20 | 20 | 30 |  |  | 20 | 15 | 20 | 20
Calculated Pump Power (Each) (kW) | [5 empty] | 0.53773 |  |  | 30% |  |  | hydrotherapentic shower |  |  | 400
[6 empty] | 1 | [5 empty] | hubbard bath |  |  | 600
[12 empty] | leg bath |  |  | 100
[12 empty] | arm bath |  |  | 35
[12 empty] | sitz bath |  |  | 30
[12 empty] | continuous flow bath |  |  | 165
[12 empty] | circular wash sink |  |  | 20 | 20 |  | 30 | 20 |  | 30
[12 empty] | semicircular wash sink |  |  | 10 | 10 |  | 15 | 10 |  | 15
[12 empty] | DEMAND FACTOR | 0.3 | 0.3 | 0.25 | 0.25 | 0.4 | 0.4 | 0.3 | 0.3 | 0.4 | 0.4
[12 empty] | STORAGE CAPACITY Factor | 1.25 | 0.9 | 0.6 | 0.8 | 1 | 1 | 2 | 0.7 | 1 | 0
Piping Heat Loss
[12 empty] | Nominal pipe size |  | Insulated Pipe |  | Bare Pipe
[16 empty] | Sch40 |  | brass | k-copper
[12 empty] | 1/2" |  | 15 |  | 35 |  | 26 | 19
[12 empty] | 3/4" |  | 17 |  | 43 |  | 32 | 26
[12 empty] | 1" |  | 19 |  | 53 |  | 38 | 32
[12 empty] | 1-1/4" |  | 21 |  | 65 |  | 46 | 39
[12 empty] | 1-/2" |  | 25 |  | 73 |  | 53 | 46
[12 empty] | 2" |  | 28 |  | 91 |  | 65 | 58
[12 empty] | 2-1/2" |  | 32 |  | 108 |  | 75 | 68
[12 empty] | 3" |  | 38 |  | 129 |  | 90 | 81
[12 empty] | 4" |  | 46 |  | 163 |  | 113 | 103
[12 empty] | 5" |  | 55 |  | 199 |  | 138 | 127
[12 empty] | 6" |  | 63 |  | 233 |  | 161 | 149
[12 empty] | 8" |  | 80 |  | 299 |  | 201 | 188

## HELPER
Insert Pipe Length & Size For Supply Network as We Don`t Know the Return Pipe Size | [7 empty] | Pressure drop = 2ft/100ft |  | pipe size with friction (1 - 4) ft/100ft at 60° F & sch. 40 brass, copper and plastic |  | friction losses values / unit length
[8 empty] | values can be selected from tables of pressure drops - ASPE |  |  |  | 1ft/100t | 2ft/100t | 3ft/100t | 4ft/100t
| Pipe Diameter |  |  | Length in meter | Q loss |  | Q loss HWR |  |  | PIPE SIZE (INCH) | Q - RANGE (GPM) | (GPM) RANGE | (GPM) RANGE | (GPM) RANGE | (GPM) RANGE
| Pipe Diameter |  |  | Length in meter | Length in meter |  |  | PIPE SIZE (IN) | (GPM) RANGE | 0.5 | 0.8 to 1.8 | 0.70887 | 1.0025 | 1.2278 | 1.4177
| Length of 1/2 " pipe |  |  | 500 | 7500 |  |  | 0.5 | 1.8 | 0.75 | 1.8 to 6.6 | 1.9534 | 2.7626 | 3.3834 | 3.9069
| Length of 3/4 " pipe |  | = | 220 | 3740 |  |  | 0.75 | 3.5 | 1 | 3.6 to 11 | 4.01 | 5.671 | 6.9455 | 8.02
| Length of 1 " pipe |  | = | 400 | 7600 |  |  | 1 | 6.6 | 1.25 | 7.2 to 18 | 7.0052 | 9.9068 | 12.1333 | 14.0104
| Length of 1-1/4 " pipe |  | = | 332 | 6972 |  |  | 1.25 | 12.4 | 1.5 | 12 to 25 | 11.0503 | 15.6274 | 19.1396 | 22.1005
| Length of 1-1/2 " pipe |  | = | 232 | 5800 |  |  | 1.5 | 18.3 | 2 | 22 to 42 | 22.684 | 32.08 | 39.2898 | 45.368
| Length of 2 " pipe |  | = | 220 | 6160 |  |  | 2 | 34.6 | 2.5 | 35 to 75 | 39.6273 | 56.0415 | 68.6365 | 79.2546
| Length of 2-1/2 " pipe |  | = | 205 | 6560 |  |  | 2.5 | 56 | 3 | 62 to 135 | 62.5097 | 88.4021 | 108.27 | 125.0194
| Length of 3 " pipe |  | = | 200 | 7600 |  |  | 3 | 93 | 4 | 135 to 280 | 128.32 | 181.4719 | 222.2568 | 256.64
| Length of 4 " pipe |  | = | 100 | 4600 |  |  | 4 | 181 | 5 | 240 to 490 | 224.1658 | 317.0183 | 388.2666 | 448.3316
| Length of 5" pipe |  | = | 100 | 5500 |  |  |  |  | 6 | 380 to 800 | 353.6083 | 500.0777 | 612.4676 | 707.2167
| Length of 6 " pipe |  | = | 130 | 8190 |  |  |  |  | 8 | 800 to 1700 | 725.8875 | 1026.56 | 1257.2741 | 1451.7751
| Length of 8 " pipe |  | = | 150 | 12000 |  |  |  |  | 10 | 1500 to 3100 | 1268.0733 | 1793.3265 | 2196.3675 | 2536.1467
| Total Heat loss From Supply Pipes |  |  |  | 82222 |  | 54814.6667 |  |  | 12 | 2400 to 5000 | 2000.3108 | 2828.8667 | 3464.64 | 4000.6217
[10 empty] | 14 | 3000 to 6400 | 2940.793 | 4158.9094 | 5093.603 | 5881.5861
Assume the heat loss from return pipes equal to 2/3 heat loss from supply pipes | [9 empty] | 16 | 4400 to 9000 | 4106.24 | 5807.1003 | 7112.2163 | 8212.48
[10 empty] | 18 | 6000 to 12500 | 5512.2085 | 7795.44 | 9547.4252 | 11024.417
Q loss in all system = |  | 137036.6667 | Btu/Hr | [6 empty] | 20 | 8000 to 17000 | 7173.3061 | 10144.5867 | 12424.5306 | 14346.6121
for every 10,000 btu/ hr ------------------------------> 1 GPM of Hot water | [5 empty] | at 20° F Temp. Drop
GPM Required = |  | 13.7 | GPM
|  | 14 | GPM | [7 empty] | For brass or copper pipe (Equation 11-24):
q = 40.1 d^2.5*(h/l)^0.5
For galvanized iron or steel pipe (Equation 11-26):
where q =gpm
q = 28.3 d^2.5*(h/l)^0.5
d = actual internal diameter of pipe, in.
h = total head available for friction loss, ft
L = equivalent length of run, ft
as per ASPE alfreed steele

## STD PIPE SIZE
PIPE CONVERSION CHART
|  | Sl No. | Steel pipe |  |  | PPR pipe ( Romafaser SDR 7.4/S 3.2) |  |  | Pipe size inch | Plastic Adsani ID | PB ID | PPR ID | CU
|  |  | Pipe size | ID | OD | Pipe size | ID | OD
|  | 1 | 15 | 15.76 | 21.3 | 0 | 0 | 0 | 0.5 | 0 | 0 | 0 | 13.3858 |  |  |  | cu
|  | 2 | 20 | 20.96 | 26.7 | 20 | 14.4 | 20 | 0.75 | 17 | 14.4 | 14.4 | 18.923 |  |  | 0.24417 | 0.527 | 13.3858
|  | 3 | 25 | 26.64 | 33.4 | 25 | 18 | 25 | 1 | 21.2 | 20.4 | 18 | 25.273 |  |  | 0.38151 | 0.745 | 18.923
|  | 4 | 32 | 35.08 | 42.2 | 32 | 23.2 | 32 | 1.25 | 27.2 | 26.2 | 23.2 | 31.623 |  |  | 0.63378 | 0.995 | 25.273
|  | 5 | 40 | 40.94 | 48.3 | 40 | 29 | 40 | 1.5 | 34 | 32.6 | 29 | 37.6174 |  |  | 0.99028 | 1.245 | 31.623
|  | 6 | 50 | 52.48 | 60.3 | 50 | 36.2 | 50 | 2 | 42.6 | 40.8 | 36.2 | 49.7586 |  |  | 1.543 | 1.481 | 37.6174
|  | 7 | 65 | 62.68 | 73 | 63 | 45.8 | 63 | 2.5 | 53.6 | 51.4 | 45.8 | 61.849 |  |  | 2.47 | 1.959 | 49.7586
|  | 8 | 75 | 77.92 | 88.9 | 75 | 54.4 | 75 | 3 | 63.8 | 61.4 | 54.4 | 73.8378 |  |  | 3.4846 | 2.435 | 61.849
|  | 9 | 90 | 90.2 | 101.6 | 90 | 60 | 90 | 3.5 | 76.6 | 73.6 | 65.4 | 85.979 |  |  | 4.239 | 2.907 | 73.8378
|  | 10 | 100 | 102.26 | 114.3 | 110 | 79.8 | 110 | 4 |  | 90 | 79.8 | 97.9678 |  |  | 7.4984 | 3.385 | 85.979
|  | 11 | 125 | 128.8 | 141.3 | 125 | 90.8 | 125 | 5 |  | 102.2 | 90.8 | 122.047 |  |  | 9.7081 | 3.857 | 97.9678
|  | 12 | 150 | 154.08 | 168.3 | 160 | 116.2 | 160 | 6 |  | 130.8 | 116.2 | 145.8214 |  |  | 15.8991 | 4.805 | 122.047
|  | 13 | 200 | 202.74 | 219.1 | 200 | 145.2 | 200 | 8 |  |  | 145.2 | 192.6082 |  |  | 24.8253 | 5.741 | 145.8214
|  | 14 | 250 | 254.46 | 273 | 250 | 181.6 | 250 | 10 |  |  | 181.6 | 240.0046 |  |  | 38.8323 | 7.583 | 192.6082
|  | 15 | 300 | 303.28 | 323.9 | 0 | 0 | 0 | 12 |  |  | 0 |  |  |  |  | 9.449 | 240.0046
[5 empty] | Sl No. | PPR pipe ( Romafaser SDR 7.4/S 3.2) |  |  | Pipe size inch |  | PREF. | FIXTURES | Weight in Fixture Units |  |  | Quantity
[6 empty] | Pipe size | ID | OD |  |  |  |  | Cold | Hot | Total
[5 empty] | 1 | 0 | 0 | 0 | 0.5 |  | #REF! | Water Closet, Private | 2.2 | 0 | 2.2 | #REF!
[5 empty] | 2 | 20 | 14.4 | 20 | 0.75 |  | #REF! | Water Closet, Public | 5 | 0 | 5 | #REF!
[5 empty] | 3 | 25 | 18 | 25 | 1 |  | #REF! | Wash Basin, Private | 0.5 | 0.5 | 0.7 | #REF!
[5 empty] | 4 | 32 | 23.2 | 32 | 1.25 |  | #REF! | Wash Basin, Public | 1.5 | 1.5 | 2 | #REF!
[5 empty] | 5 | 40 | 29 | 40 | 1.5 |  | #REF! | Service Sink | 2.25 | 2.25 | 3 | #REF!
[5 empty] | 6 | 50 | 36.2 | 50 | 2 |  | #REF! | Pantry Sink, PB | 3 | 3 | 4 | #REF!
[5 empty] | 7 | 63 | 45.8 | 63 | 2.5 |  | #REF! | Mob Sink | 1.5 | 1.5 | 2 | #REF!
[5 empty] | 8 | 75 | 54.4 | 75 | 3 |  | #REF! | Ablution, Public | 1.5 | 1.5 | 2 | #REF!
[5 empty] | 9 | 90 | 60 | 90 | 3.5 |  | #REF! | Hose Bibe | 2.5 | 0 | 0 | #REF!
[5 empty] | 10 | 110 | 79.8 | 110 | 4 |  | #REF! | Hose Bibe each additional | 1 | 0 | 0 | #REF!
[5 empty] | 11 | 125 | 90.8 | 125 | 5
[5 empty] | 12 | 160 | 116.2 | 160 | 6 |  |  | From IPC Table E103.3(2)
[5 empty] | 13 | 200 | 145.2 | 200 | 8 |  |  | FLUSH TANK SYSTEM
[5 empty] | 14 | 250 | 181.6 | 250 | 10 |  |  | Fixture | CW | HW | WS
[12 empty] | Type | FU | FU | FU
[12 empty] | Private Lavatory | 0.5 | 0.5 | 0.75
[12 empty] | Public Lavatory | 1.5 | 1.5 | 2
|  |  | FIXTURE | MINIMUM PIPE SIZE (inch) | MINIMUM PIPE SIZE (inch) | MINIMUM PIPE SIZE (mm) | [5 empty] | Water Closet (Flush T) | 2 | 0 | 2
|  |  | Bathtubsa (60" x 32" and smaller) | 1/2 | 0.5 | 15 | [5 empty] | Private Shower | 1 | 1 | 1.4
|  |  | Bathtubsa (larger than 60" x 32") | 1/2 | 0.5 | 15 | [5 empty] | Public Shower | 3 | 3 | 4
|  |  | Bidet | 3/8 | 0.375 | 12 | [5 empty] | Lab/Service Sink | 2.25 | 2.25 | 3
|  |  | Combination sink and tray | 1/2 | 0.5 | 15 | [5 empty] | Hose Bibb | 2.5 | 0 | 2.5
|  |  | Dishwasher, domestica | 1/2 | 0.5 | 15 | [5 empty] | Hose Bibb (each additional) | 1 | 0 | 1
|  |  | Drinking fountain | 3/8 | 0.375 | 12 | [5 empty] | Kitchen Sink (PRV.) | 1 | 1 | 1.4 | ASPE & IPC
|  |  | Hose bibbs | 1/2 | 0.5 | 15 |  | Pantry Sink | 3 | 3 | 4 | Kitchen Sink (PUB.) | 3 | 3 | 4
|  |  | Kitchen sinka | 1/2 | 0.5 | 15 | [5 empty] | Janitor | 1.5 | 0 | 1.5
|  |  | Laundry, 1, 2 or 3 compartmentsa | 1/2 | 0.5 | 15 | [5 empty] | Pantry Sink | 1.5 | 1.5 | 2
|  |  | Lavatory | 3/8 | 0.375 | 12 | [5 empty] | ABBLIUTION | 1.5 |  | 1.5
|  |  | Shower, single heada | 1/2 | 0.5 | 15 | [5 empty] | Mob Sink, PR | 1.5 | 1.5 | 2 | UPC
|  |  | Sinks, flushing rim | 3/4 | 0.75 | 20 | [5 empty] | Mob Sink, PB | 3 | 3 | 4
|  |  | Sinks, service | 1/2 | 0.5 | 15
|  |  | Urinal, flush tank | 1/2 | 0.5 | 15 | [5 empty] | Sink - Pantry 1.5 | flat | ASPE
|  |  | Urinal, flush valve | 3/4 | 0.75 | 20 | [5 empty] | Sink - Pantry 2.5 | restaurant
|  |  | Wall hydrant | 1/2 | 0.5 | 15
|  |  | Water closet, flush tank | 3/8 | 0.375 | 12 | [5 empty] | Drinking fountain-Dispenser ICE | 0.25 | 0 | 0.25
|  |  | Water closet, flush valve | 1 | 1 | 25 | [5 empty] | Hand spray | 2 | 0 | 2
|  |  | Water closet, flushometer tank | 3/8 | 0.375 | 12
|  |  | Water closet, one piecea | 1/2 | 0.5 | 15
TABLE E103.3(5) ALLOWANCE IN EQUIVALENT LENGTHS OF PIPE FOR FRICTION LOSS IN VALVES AND THREADED FITTINGS (feet)
FITTING OR VALVE |  |  | PIPE SIZE (inches)
|  |  | 1/2 |  | 3/ 4 |  | 1 |  | 11/ 4 |  | 11/ 2 |  | 2 |  | 21/ 2 | 3
45-degree elbow |  |  | 1.2 |  | 1.5 |  | 1.8 |  | 2.4 |  | 3 |  | 4 |  | 5 | 6
90-degree elbow |  |  | 2 |  | 2.5 |  | 3 |  | 4 |  | 5 |  | 7 |  | 8 | 10
Tee, run |  |  | 0.6 |  | 0.8 |  | 0.9 |  | 1.2 |  | 1.5 |  | 2 |  | 2.5 | 3
Tee, branch |  |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 10 |  | 12 | 15
Gate valve |  |  | 0.4 |  | 0.5 |  | 0.6 |  | 0.8 |  | 1 |  | 1.3 |  | 1.6 | 2
Balancing valve |  |  | 0.8 |  | 1.1 |  | 1.5 |  | 1.9 |  | 2.2 |  | 3 |  | 3.7 | 4.5
Plug-type cock |  |  | 0.8 |  | 1.1 |  | 1.5 |  | 1.9 |  | 2.2 |  | 3 |  | 3.7 | 4.5
Check valve, swing |  |  | 5.6 |  | 8.4 |  | 11.2 |  | 14 |  | 16.8 |  | 22.4 |  | 28 | 33.6
Globe valve |  |  | 15 |  | 20 |  | 25 |  | 35 |  | 45 |  | 55 |  | 65 | 80
Angle valve |  |  | 8 |  | 12 |  | 15 |  | 18 |  | 22 |  | 28 |  | 34 | 40
For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 degree = 0.0175 rad.
TABLE E103.3(6) PRESSURE LOSS IN FITTINGS AND VALVES EXPRESSED AS EQUIVALENT LENGTH OF TUBEa (feet)
NOMINAL OR STANDARD SIZE (inches) | FITTINGS | [6 empty] | Coupling |  | VALVES
| Standard Ell |  |  | gO-Degree Tee | [5 empty] | Ball |  | Gate |  | Butterfly |  | Check
| gO Degree | 45 Degree |  | Side Branch |  | Straight Run
3/ 8 | 0.5 | - |  | 1.5 |  | - |  | - |  | - |  | - |  | - |  | 1.5
1/2 | 1 | 0.5 |  | 2 |  | - |  | - |  | - |  | - |  | - |  | 2
5/8 | 1.5 | 0.5 |  | 2 |  | - |  | - |  | - |  | - |  | - |  | 2.5
3/4 | 2 | 0.5 |  | 3 |  | - |  | - |  | - |  | - |  | - |  | 3
1 | 2.5 | 1 |  | 4.5 |  | - |  | - |  | 0.5 |  | - |  | - |  | 4.5
11/ 4 | 3 | 1 |  | 5.5 |  | 0.5 |  | 0.5 |  | 0.5 |  | - |  | - |  | 5.5
11/ 2 | 4 | 1.5 |  | 7 |  | 0.5 |  | 0.5 |  | 0.5 |  | - |  | - |  | 6.5
2 | 5.5 | 2 |  | 9 |  | 0.5 |  | 0.5 |  | 0.5 |  | 0.5 |  | 7.5 |  | 9
21/ 2 | 7 | 2.5 |  | 12 |  | 0.5 |  | 0.5 |  | - |  | 1 |  | 10 |  | 11.5
3 | 9 | 3.5 |  | 15 |  | 1 |  | 1 |  | - |  | 1.5 |  | 15.5 |  | 14.5
31/ 2 | 9 | 3.5 |  | 14 |  | 1 |  | 1 |  | - |  | 2 |  | - |  | 12.5
4 | 12.5 | 5 |  | 21 |  | 1 |  | 1 |  | - |  | 2 |  | 16 |  | 18.5
5 | 16 | 6 |  | 27 |  | 1.5 |  | 1.5 |  | - |  | 3 |  | 11.5 |  | 23.5
6 | 19 | 7 |  | 34 |  | 2 |  | 2 |  | - |  | 3.5 |  | 13.5 |  | 26.5
8 | 29 | 11 |  | 50 |  | 3 |  | 3 |  | - |  | 5 |  | 12.5 |  | 39
For SI: 1 inch = 25.4 mm, 1 foot = 304.8 mm, 1 degree = 0.01745 rad. a. Allowances are for streamlined soldered fittings and recessed threaded fittings. For threaded fittings, double the allowances shown in the table. The equivalent lengths presented above are based on a C factor of 150 in the Hazen-Williams friction loss formula. The lengths shown are rounded to the nearest half-foot.